# Lime Wood Hotel & Spa

## Roca GPA 400 Boiler Technical Dossier (Enhanced)

This document has been expanded with engineering procedures and diagram sections. Manufacturer wiring diagrams and exploded parts drawings are not reproduced here because they are proprietary and model/revision specific. Insert the correct OEM drawings for the exact boiler revision when obtained.

## Wiring Diagram Section

Required OEM drawings:
• Power supply and isolation
• Burner management controller
• Ignition transformer
• Flame probe circuit
• Gas valve circuit
• Fan motor circuit
• Flow and return temperature sensors
• High limit thermostat
• BMS enable/disable terminals
• Alarm and volt-free contacts

Document Reference: To be populated with the official Roca GPA 400 wiring drawing for the installed revision.

## Exploded Parts Drawing Section

Required OEM exploded drawings:
• Heat exchanger assembly
• Burner assembly
• Fan assembly
• Gas train
• Control panel
• Electrical enclosure
• Door and insulation
• Safety devices
• Casing components

Document Reference: Insert the official Roca exploded parts catalogue matching the appliance serial number.

## Detailed Maintenance Procedure

1. Notify BMS users and isolate the boiler if required.

2. Shut off gas supply and electrical supply using lock-off procedures.

3. Allow boiler to cool.

4. Remove front casing and inspect insulation and combustion chamber.

5. Inspect burner, ignition electrode and flame probe. Clean or replace as required.

6. Inspect heat exchanger for fouling or corrosion.

7. Check gas valve, pipework and test for leaks after reassembly.

8. Inspect fan and air intake for debris and free rotation.

9. Check safety thermostat, temperature sensors and pressure devices.

10. Inspect electrical terminals for overheating or loose connections.

11. Reassemble using new seals where required.

12. Restore power and gas supply.

13. Carry out combustion analysis and adjust only in accordance with manufacturer instructions.

14. Test flame failure, high limit protection and lockout functions.

15. Verify operation under BMS control.

16. Record combustion readings, parts replaced and observations in the service history.

## Future Inserts

Once the exact boiler revision is confirmed, replace these placeholders with the official OEM wiring diagrams, exploded parts catalogue and illustrated service manual.