# Lime Wood Hotel & Spa

## Remaining Pumps Technical Dossier

Staff House Boiler Room

## Asset Summary

| Asset ID | Manufacturer | Model | Serial Number |
| --- | --- | --- | --- |
| P/SH/10 | Onyx | RS25/6G-130 | P11-2022-06 |
| P/SH/12 | Onyx | RS25/6G-130 | P11-2022-11 |
| P/SH/11 | Grundfos | UPS 15-50 | 97549426 |

## System Function

These pumps provide circulation to dedicated heating and hot water circuits within the Staff House Boiler Room. They maintain system flow and ensure efficient heat distribution.

## Operation

The pumps are energised by local controls or the BMS depending on system demand. Correct rotation, adequate system pressure and open isolation valves are required before operation.

## Routine Maintenance

Weekly: Inspect for leaks, noise and vibration.
Monthly: Check electrical connections, operating temperature and pump body condition.
Annually: Verify insulation resistance, confirm rotation, inspect bearings (where applicable), clean strainers and record running current.

## Safe Isolation

Switch off and lock off the electrical supply. Close suction and discharge isolation valves. Allow the pump to cool before draining and removing.

## Replacement Procedure

Drain the isolated section, remove flange bolts/unions, replace gaskets, install the replacement pump in the correct flow direction, refill, vent, restore power and confirm operation.

## Fault Finding

No flow: airlock, seized rotor or closed valve.
Noise: cavitation or bearing wear.
Trips: overload or motor fault.
Low flow: blocked strainer or incorrect speed setting.

## Recommended Critical Spares

Flange gaskets, terminal box components, capacitors (where fitted), impeller assemblies, isolation valve seals and spare circulation pump for critical services.

## Engineer Notes

Record flow and return temperatures, running current and any vibration observations during each planned maintenance inspection.