# Lime Wood Hotel & Spa

## Expansion Vessel Technical Dossier

Staff House Boiler Room

## Covered Assets

| Asset ID | Manufacturer | Model | Serial Number |
| --- | --- | --- | --- |
| EV/SH/1 | Reflex | N8 | 2013575A244056953 |
| EV/SH/2 | Wilo | XT-600V | 53027 |
| EV/SH/3 | Lowara | 110-Ultra-Pro | 26-000000141930 |

## System Function

Expansion vessels absorb the increase in water volume caused by thermal expansion, maintaining stable pressure and preventing nuisance operation of safety valves and pressurisation equipment.

## Construction

Steel pressure vessel with an internal diaphragm separating system water from the nitrogen/air pre-charge.

## Routine Inspection

Weekly: Check for external leaks or damage.
Monthly: Inspect supports and connections.
Annually: Isolate, drain water side, measure and adjust pre-charge, inspect diaphragm performance and reconnect after successful pressure testing.

## Pre-charge Procedure

1. Isolate the vessel.
2. Drain the water side completely.
3. Measure gas pre-charge at the Schrader valve.
4. Adjust to the design value specified for the heating system.
5. Refill and vent the system.
6. Confirm stable operating pressure.

## Replacement Procedure

Lock off and isolate, drain pressure, disconnect pipework, remove vessel safely, install replacement with new sealing materials, recharge to the specified pre-charge, refill, vent and recommission.

## Common Faults

Loss of pre-charge, ruptured diaphragm, waterlogged vessel, external corrosion, leaking Schrader valve, undersized vessel causing frequent pressure fluctuations.

## Recommended Critical Spares

Schrader valve core, valve cap, connection gasket, replacement diaphragm (where serviceable), pressure gauge, isolation valve seals.

## Annual Service Checklist

□ External condition
□ Support brackets
□ Connection tightness
□ Pre-charge recorded
□ System pressure restored
□ Leak test completed
□ Results entered into maintenance records

## Engineer Notes

Record the measured pre-charge, cold fill pressure and operating pressure at every annual inspection. Frequent topping up of the heating system should be investigated for leaks.