# Lime Wood Hotel & Spa

## HydroTec Water Treatment Unit Technical Dossier

Staff House Boiler Room

| Field | Value |
| --- | --- |
| Asset ID | WT/SH/1 (verify against asset register) |
| Manufacturer | HydroTec |
| Equipment | Water Treatment Unit |
| Model | From asset register |
| Serial Number | From asset register |
| Location | Staff House Boiler Room |
| Criticality | Medium-High |

## System Function

Maintains heating water quality by reducing scale formation and corrosion, helping protect boilers, pumps, valves and heat exchangers while improving system efficiency.

## Associated Equipment

Boilers, circulation pumps, plate heat exchanger, pressurisation unit, expansion vessel, strainers and dosing points.

## Normal Operation

System water passes through the HydroTec treatment unit where conditioning media or treatment technology reduces fouling and supports long-term water quality.

## Routine Maintenance

Weekly: Inspect for leaks and verify normal operation.
Monthly: Check isolation valves, connections and treatment status.
Quarterly: Inspect treatment media or cartridges where applicable.
Annually: Full inspection, clean housing, replace consumables if required and record water quality results.

## Water Quality Checks

Record system pressure, pH, conductivity (where applicable), inhibitor concentration, glycol concentration (if used) and visual water condition.

## Isolation Procedure

Close upstream and downstream isolation valves, relieve pressure, drain the unit before opening any housing or removing consumables.

## Fault Finding

No flow: blocked strainer or closed valve.
Poor water quality: exhausted treatment media or incorrect dosing.
Leaks: damaged seals or loose unions.
High pressure drop: fouled treatment element.

## Recommended Critical Spares

Seal kit
Replacement treatment media/cartridges
Isolation valve gaskets
Drain valve seals
Pressure gauge (if fitted)

## Engineer Notes

Maintain water-treatment records alongside PPM records. Any additions of fresh water should be investigated and inhibitor levels rechecked.