# Lime Wood Hotel & Spa

## PU/SH/2 - Wilo 255D Pressurisation Unit

Engineering Technical Dossier

| Field | Value |
| --- | --- |
| Asset ID | PU/SH/2 |
| Manufacturer | Wilo |
| Equipment | Pressurisation Unit |
| Model | 255D |
| Serial Number | B05062278 |
| Location | Staff House Boiler Room |
| Criticality | High |

## System Function

The pressurisation unit maintains the sealed heating system pressure automatically, replaces small water losses and helps protect the system from low-pressure lockouts.

## Main Components

• Control panel
• Pressure transducer
• Break tank
• Filling solenoid valve
• Pump assembly
• Non-return valve
• Isolation valves
• Flexible connection

## Normal Operation

1. System pressure is continuously monitored.
2. When pressure falls below the set point the filling pump/valve operates.
3. Water is added until the target pressure is restored.
4. The unit returns to standby and monitors the system.

## Routine Maintenance

Weekly:
• Check displayed pressure.
• Check for alarms.
• Inspect for leaks.

Monthly:
• Inspect electrical connections.
• Check break tank condition.
• Verify automatic fill operation.

Annually:
• Inspect pressure sensor.
• Test alarms.
• Verify pressure settings.
• Inspect all pipework and valves.

## Commissioning

Confirm electrical supply, fill and vent the heating system, set the required cold fill pressure, verify automatic operation and record final settings.

## Fault Finding

Low pressure: check leaks, expansion vessel charge or filling circuit.
No automatic fill: check power, controls and inlet supply.
Frequent filling: investigate system leaks or failed expansion vessel.

## Recommended Spares

Pressure sensor
Filling solenoid valve
Pump assembly
Control PCB (if applicable)
Float switch
Fuse kit
Flexible hose washers

## Engineer Notes

Refer to the official Wilo installation and operating instructions for model-specific settings and parameter values.

# EV/SH/2 - Wilo XT-600V Expansion Vessel

| Field | Value |
| --- | --- |
| Asset ID | EV/SH/2 |
| Manufacturer | Wilo |
| Equipment | Expansion Vessel |
| Model | XT-600V |
| Serial Number | 53027 |
| Location | Staff House Boiler Room |
| Criticality | High |

## System Function

The expansion vessel accommodates thermal expansion of the heating water and stabilises system pressure.

## Construction

Steel pressure vessel with replaceable diaphragm separating system water from the pre-charged gas cushion.

## Routine Maintenance

Monthly visual inspection for leaks and corrosion.
Annually isolate, drain water side, verify and adjust pre-charge pressure, inspect diaphragm condition before returning to service.

## Replacement Procedure

Isolate vessel, relieve water pressure, disconnect, fit replacement vessel, recharge to specified pre-charge, refill and vent the system.

## Common Faults

Loss of pre-charge, ruptured diaphragm, corrosion, leaking connection, incorrect sizing.

## Recommended Spares

Schrader valve core
Valve cap
Connection gasket
Replacement diaphragm (if serviceable model)

## Engineer Notes

Record pre-charge pressure and inspection results during every annual service.