# Lime Wood Hotel & Spa

## Plate Heat Exchanger Technical Dossier

Staff House Boiler Room

## Asset Details

| Field | Value |
| --- | --- |
| Asset ID | HX/sh/1 |
| Equipment | Plate Heat Exchanger |
| Manufacturer | From asset register |
| Model | HX/sh/1 |
| Serial Number | See asset register |
| Location | Staff House Boiler Room |
| Criticality | High |

## System Function

The plate heat exchanger transfers heat between the primary and secondary heating circuits while preventing the two water systems from mixing.

## Main Components

Fixed frame, pressure plate, heat transfer plates, gaskets, tie bolts, inlet/outlet connections and support feet.

## Normal Operation

Primary hot water passes through alternating plates while secondary water flows in the opposite direction, providing efficient counter-flow heat transfer.

## Routine Maintenance

Weekly: inspect for leaks and record temperatures. Monthly: inspect gaskets, supports and differential temperatures. Annually: isolate, inspect plates, clean fouling, renew damaged gaskets, pressure test before returning to service.

## Isolation Procedure

Shut down pumps, isolate both primary and secondary circuits, allow to cool, relieve pressure, drain both sides before dismantling.

## Fault Finding

Poor performance: fouled plates or low flow. External leak: failed gasket or loose tie bolts. Cross contamination: damaged plate. High pressure drop: blocked passages.

## Recommended Critical Spares

Gasket set, plate pack (where practical), tie bolts and nuts, vent and drain seals, thermometer pockets.

## Engineer Notes

Record primary and secondary flow/return temperatures during every planned maintenance visit to monitor efficiency.