LIME WOOD HOTEL & SPA

PRESSURISATION UNIT TECHNICAL DOSSIER

Staff House Boiler Room | PU/SH/1

# 1. Asset Identification

| Field | Value |
| --- | --- |
| Asset ID | PU/SH/1 |
| Equipment | Pressurisation Unit |
| Recorded manufacturer / supplier | Tricell |
| Recorded model | Minipress 230 |
| Serial number | SN364245 |
| Location | Staff House Boiler Room |
| Duty | Sealed heating-system pressurisation |
| Identification status | Model appears consistent with Flamco Flexfiller MiniPress 230 supplied/listed by Tricel Pumps. Verify against equipment nameplate before ordering parts. |

# 2. Equipment Function

The unit maintains the minimum pressure required in a sealed heating system. It monitors system pressure electronically and introduces small quantities of mains water through an internal Category 5 break arrangement when pressure falls below the configured set point.

# 3. Verified Product-Family Data

| Field | Value |
| --- | --- |
| Configuration | MiniPress 230 twin-pump version |
| Nominal electrical supply | 230 V, single phase, 50 Hz |
| Top-up flow | Approximately 0.5 litres/minute at 1 bar |
| Permitted delivery-pressure range | 0.7 to 3.0 bar |
| Maximum delivery pressure | 3.0 bar |
| System pressure rating | PN6 |
| System-water temperature range | 5 to 85 °C |
| Mains-water temperature range | 5 to 45 °C |
| Mains pressure range | 0.5 to 6.0 bar |
| Backflow protection | Visible AB air gap / Category 5 break tank |
| Controls | Electronic pressure transducer and microprocessor |
| External indication | Common alarm volt-free contact; model family may support Modbus RTU depending on revision |

Important: values above relate to the published MiniPress 230 product family. The equipment nameplate and installed manual take priority.

# 4. Main Components

Powder-coated wall-mounted enclosure

Internal break tank with visible air gap

Twin low-flow top-up pumps

Electronic pressure transducer

Microprocessor controller and display

Mains-water inlet and system top-up outlet

Overflow connection

Common alarm contacts

Internal non-return and isolation components

# 5. Normal Sequence of Operation

The controller continuously reads sealed-system pressure.

When pressure falls below the configured start threshold, the duty pump starts.

Water is drawn from the internal break tank and delivered into the heating system.

The pump stops when the configured pressure is restored.

The standby pump is available for alternation or backup, depending on controller configuration.

A prolonged run, excessive starts, low water level or control fault generates an alarm.

# 6. Safe Isolation

Notify affected building users and the BMS operator.

Record the displayed system pressure and active alarms.

Isolate and lock off the 230 V electrical supply.

Close the mains-water inlet isolation valve.

Close the top-up outlet isolation valve to the heating system.

Relieve trapped hydraulic pressure carefully and confirm zero energy before opening the enclosure or disconnecting pipework.

# 7. Commissioning / Recommissioning

Confirm the unit is securely mounted and all pipework is supported.

Confirm the overflow is unobstructed and terminates visibly and safely.

Open the mains-water inlet and inspect the break tank filling arrangement.

Confirm the sealed heating system has been initially filled and vented.

Restore electrical power.

Enter the required cold-fill pressure and permitted differential settings using the installed manual.

Test each pump individually where the controls allow.

Verify automatic top-up, pump stop, common alarm and BMS indication.

Record set points, system cold pressure and final operating status.

# 8. Planned Maintenance

## Weekly / Routine Visual Check

Check display pressure and alarm state.

Inspect enclosure and pipework for leakage.

Confirm overflow is dry during normal operation.

Listen for abnormal pump noise.

Investigate frequent top-up operation rather than treating it as normal.

## Quarterly

Test duty and standby pump operation.

Test common alarm output.

Inspect break tank, float/level arrangement and visible air gap.

Inspect electrical connections for heat damage or looseness.

Check inlet and outlet isolating valves for correct position.

## Annual Service

Clean and inspect break tank and overflow path.

Verify pressure-transducer reading against a calibrated gauge.

Test low-pressure start, stop pressure, excessive-run protection and alarm functions.

Check both pumps for leaks, noise and delivery performance.

Inspect non-return valves and internal flexible connections.

Check protective device and earth continuity as required by site electrical procedures.

Review top-up history because high usage usually indicates system leakage or expansion-vessel failure.

Record all settings and results.

# 9. Fault Finding

| Symptom | Likely Causes | Checks / Corrective Action |
| --- | --- | --- |
| Low-pressure alarm | System leak; failed expansion vessel; top-up unit isolated | Inspect system, verify vessel pre-charge, check inlet/outlet isolations. |
| Pump runs but pressure does not rise | No water in break tank; airlock; failed pump; non-return valve fault | Check mains supply and break tank level; vent/check pump; test delivery. |
| Frequent pump starts | Leakage; incorrect pressure band; expansion vessel waterlogged | Check settings, leak-test system and test expansion vessels. |
| Overflow discharging | Inlet control/float fault; excessive mains pressure | Isolate mains supply if needed and inspect inlet control components. |
| No display / no operation | Electrical isolation; fuse/protective device; controller fault | Verify 230 V supply safely and inspect internal protection. |
| Common alarm remains active | Alarm not reset; unresolved pressure/water/control fault | Read controller alarm, rectify cause and reset in accordance with manual. |

# 10. Recommended Spares / Consumables

Correct replacement pump module for MiniPress 230 revision

Pressure transducer

Inlet float or solenoid assembly, according to installed revision

Non-return valve / internal seal kit

Control fuses

Flexible hose washers and union seals

Controller/display assembly only after exact product code verification

# 11. Annual Inspection Record

| Check | Result / Reading | Action Required | Initials / Date |
| --- | --- | --- | --- |
| ☐ Nameplate and serial number verified |  |  |  |
| ☐ System pressure reading checked against calibrated gauge |  |  |  |
| ☐ Duty pump tested |  |  |  |
| ☐ Standby pump tested |  |  |  |
| ☐ Break tank and air gap inspected |  |  |  |
| ☐ Overflow tested clear |  |  |  |
| ☐ Alarm output tested |  |  |  |
| ☐ Electrical enclosure inspected |  |  |  |
| ☐ Top-up frequency reviewed |  |  |  |
| ☐ Settings and final pressure recorded |  |  |  |

# 12. Manufacturer Documentation References

Reference documents used to prepare this site dossier: Tricel Pumps MiniPress data sheet and Aalberts/Flamco Flexfiller MiniPress installation and operating manual. Store the exact OEM manual matching the installed product code alongside this record.

# 13. Service History

| Date | Engineer | Work Completed | Readings / Settings | Parts Used | Next Due |
| --- | --- | --- | --- | --- | --- |