LIME WOOD HOTEL & SPA

CALORIFIER TECHNICAL DOSSIER

Staff House Boiler Room | Unknown Units CA/SH/1 to CA/SH/3

# 1. Asset Identification

| Asset ID | Equipment | Manufacturer | Model | Serial Number | Identification Status |
| --- | --- | --- | --- | --- | --- |
| CA/SH/1 | Calorifier | Unknown Unit | Unknown Unit | Unknown Unit | Data plate and capacity to be surveyed |
| CA/SH/2 | Calorifier | Unknown Unit | Unknown Unit | Unknown Unit | Data plate and capacity to be surveyed |
| CA/SH/3 | Calorifier | Unknown Unit | Unknown Unit | Unknown Unit | Data plate and capacity to be surveyed |

These three calorifiers are intentionally retained as separate database assets. No manufacturer, model, capacity, pressure rating or serial number is assumed until each data plate has been photographed and verified.

# 2. System Function

A calorifier stores and heats domestic hot water indirectly using a primary heating-water coil or heat exchanger. The vessels support the hotel domestic hot-water demand and may operate with duty sharing, staged recovery or common flow/return headers. Exact arrangement requires site confirmation.

# 3. Information Required at Survey

| Check | Result / Reading | Action Required | Initials / Date |
| --- | --- | --- | --- |
| ☐ Manufacturer and full model |  |  |  |
| ☐ Serial number and year of manufacture |  |  |  |
| ☐ Storage capacity in litres |  |  |  |
| ☐ Maximum working pressure and test pressure |  |  |  |
| ☐ Primary-coil rating and connection sizes |  |  |  |
| ☐ Secondary return connection |  |  |  |
| ☐ Immersion heater rating, if fitted |  |  |  |
| ☐ Safety valve size and set pressure |  |  |  |
| ☐ Temperature-control and high-limit devices |  |  |  |
| ☐ Inspection opening / manway details |  |  |  |
| ☐ Insulation and external-jacket condition |  |  |  |
| ☐ Asset duty and hydraulic arrangement |  |  |  |

# 4. Typical Associated Components

Cold-water inlet and isolation valve

Hot-water outlet

Secondary circulation return

Primary heating flow and return connections

Control valve and actuator

Temperature sensor / thermostat pocket

High-limit thermostat

Temperature and pressure relief or safety valve

Drain valve

Air vent

Expansion vessel and pressure-control components

Immersion heater, where fitted

# 5. Normal Operation

A domestic hot-water temperature demand is generated by the vessel sensor or BMS.

The primary heating control valve opens or the primary pump is enabled.

Heating water passes through the calorifier coil and transfers heat to the stored domestic water.

The control valve closes or pump stops at the configured storage temperature.

The secondary return maintains distribution-loop temperature where fitted.

Independent high-limit and safety devices protect against overheating and overpressure.

# 6. Routine Maintenance

## Weekly / Routine

Inspect for water leakage, corrosion and damaged insulation.

Record stored hot-water temperature and secondary-return temperature.

Confirm controls and BMS indication are normal.

Check for unusual noise, hammer or continuous safety-valve discharge.

## Monthly

Inspect valves, sensors and control actuator.

Confirm drain, vent and access points remain unobstructed.

Check supporting feet, brackets and surrounding floor condition.

Review temperature records for slow recovery or unstable control.

## Annual / Planned Shutdown

Isolate safely and allow the vessel to cool.

Test temperature-control and high-limit devices.

Inspect safety-valve discharge arrangements in accordance with site procedures and competent-person requirements.

Inspect internal condition where a suitable access opening exists and risk assessment permits.

Check for scale, corrosion, sediment and signs of microbiological fouling.

Flush sediment from the drain point where appropriate.

Inspect sacrificial anodes if fitted.

Inspect coil performance using primary and domestic-water temperature readings.

Record capacity, pressure ratings and full nameplate details if still unknown.

# 7. Safe Isolation

Notify hotel operations because domestic hot-water service may be affected.

Disable heat input and isolate the primary heating flow and return.

Isolate cold-water inlet, hot-water outlet and secondary return as required.

Isolate and lock off immersion heaters or associated electrical controls.

Allow water to cool to a safe temperature.

Relieve pressure through an approved method and confirm zero pressure before opening drains, inspection covers or fittings.

Treat stored hot water, pressure and vessel weight as significant hazards.

# 8. Fault Finding

| Symptom | Likely Causes | Checks / Corrective Action |
| --- | --- | --- |
| Slow hot-water recovery | Scaled coil; low primary flow; control valve fault; airlock | Check primary temperatures/flow, valve operation and coil condition. |
| Low stored temperature | Sensor/control fault; insufficient primary temperature; high demand | Verify sensor, set point, primary supply and load. |
| Water too hot | Control valve passing; sensor failed; thermostat set incorrectly | Test controller, actuator and independent high-limit device. |
| Safety valve discharging | Excess pressure; failed expansion vessel; overheating; valve fault | Check system pressure, expansion provision, controls and valve condition. |
| Brown or contaminated water | Internal corrosion; sediment; water-quality issue | Sample/inspect, flush as appropriate and assess vessel condition. |
| External leakage | Connection seal; drain valve; vessel corrosion | Isolate, identify source and repair or replace following condition assessment. |

# 9. Recommended Generic Spares

Do not order vessel-specific parts until the manufacturer and model are confirmed.

Temperature sensor matching the installed controls

High-limit thermostat matching the installed pocket

Control-valve actuator or service kit after identification

Drain and vent valve seals

Thermometer / gauge where fitted

Inspection-cover gasket after exact dimensions are confirmed

Sacrificial anode only after manufacturer identification

# 10. Compliance and Water Hygiene Notes

Domestic hot-water storage and distribution must be managed under the site water-safety plan. Temperature monitoring, flushing, inspection, cleaning and any legionella-control measures must follow the current risk assessment and written control scheme. Pressure-system examination requirements should be confirmed by the appointed competent person based on the installed vessel and protective equipment.

# 11. Individual Asset Inspection Records

## CA/SH/1 - Unknown Unit

| Check | Result / Reading | Action Required | Initials / Date |
| --- | --- | --- | --- |
| ☐ Data plate photographed |  |  |  |
| ☐ Capacity confirmed |  |  |  |
| ☐ Pressure rating confirmed |  |  |  |
| ☐ Safety devices identified |  |  |  |
| ☐ Primary coil connections identified |  |  |  |
| ☐ DHW and secondary-return connections identified |  |  |  |
| ☐ Condition assessed |  |  |  |
| ☐ Service date recorded |  |  |  |

## CA/SH/2 - Unknown Unit

| Check | Result / Reading | Action Required | Initials / Date |
| --- | --- | --- | --- |
| ☐ Data plate photographed |  |  |  |
| ☐ Capacity confirmed |  |  |  |
| ☐ Pressure rating confirmed |  |  |  |
| ☐ Safety devices identified |  |  |  |
| ☐ Primary coil connections identified |  |  |  |
| ☐ DHW and secondary-return connections identified |  |  |  |
| ☐ Condition assessed |  |  |  |
| ☐ Service date recorded |  |  |  |

## CA/SH/3 - Unknown Unit

| Check | Result / Reading | Action Required | Initials / Date |
| --- | --- | --- | --- |
| ☐ Data plate photographed |  |  |  |
| ☐ Capacity confirmed |  |  |  |
| ☐ Pressure rating confirmed |  |  |  |
| ☐ Safety devices identified |  |  |  |
| ☐ Primary coil connections identified |  |  |  |
| ☐ DHW and secondary-return connections identified |  |  |  |
| ☐ Condition assessed |  |  |  |
| ☐ Service date recorded |  |  |  |

# 12. Service History

| Asset ID | Date | Engineer | Work Completed | Readings | Parts Used | Next Due |
| --- | --- | --- | --- | --- | --- | --- |